## Slide 1
Better WASH for quality care in HEALTHCARE FACILITIES
Technical Module:
WATER
Insert date & location
Notes: Supplementary materials: “Virtual SI (sanitary inspection)” exercise.
If you are visiting a facility as part of the training, you do not need to complete this exercise. If you do decide to include it, you should allow 45 minutes to conduct the exercise in a classroom setting.

## Slide 2: Learning objectives
By the end of the session, participants should be able to:
  Describe the importance of water in health care facilities for provision and experience of care
  Describe minimum water quantities (and storage) required in health care facilities,
  Understand water quality risks and standards in health care facilities
  Describe approaches and interventions for incrementally improving water quantity and quality in health care facilities, including climate smart adaptations

## Slide 3: What are some of the problems linked to an inadequate water supply in health care facilities ?
Notes: You may wish to write the suggestions on a flip chart and refer back to them throughout the session.

## Slide 4: Climate impacts on water supply
Credit: IWA/Chris Wells.

## Slide 5: Climate impacts on water supply
Credit: IWA/Chris Wells.

## Slide 6: Poor water supply leads to:
No/ insufficient drinking water
Dehydration
Diarrhoea
Contaminated water
Insufficient water for hand hygiene
Insufficient water for cleaning, showers, toilets
Waterborne outbreaks
Spread of infections; risks to patient and staff safety, inability to control outbreaks
Spread of fecal contamination
Visually dirty, smells, decrease in care seeking and trust in health care
Inability to take medicines

## Slide 7: What are some of the solutions to these problems?
Rainwater harvesting
Solar powered water pumping
Elevated water storage
Sourcing additional water supplies
Water treatment
Portable drinking-water and handwashing stations
All rely on:
Leadership
Planning
Advocacy!
Notes: Most of these are big infrastructure things which will be out of reach for many – what can be done if infrastructure doesn’t exist? Make a case to district health office, local NGO?

## Slide 8: Applying a risk-based approach: WHO guidance
Guidelines
Water safety planning and climate
Regulations
Health care facilities
Water treatment performance
Principals
1.Health based targets
2. Risk assessment and risk management
3. Surveillance
Notes: Add links to documents in notes

## Slide 9: What are the main water needs (and related standards) in a health care facility?

## Slide 10: Water needs and standards
Refer to WHO UNICEF Core questions and indicators for monitoring WASH in health care facilities for definitions of “improved”
www.who.int/water_sanitation_health/publications/core-questions-and-indicators-for-monitoring-wash/en/
How might climate change affect these items?
Water should be available for
  drinking
  personal hygiene including hand washing, bathing and cleaning
  cleaning
  medical activities
  cooking
  laundry
Water must be on-site from an improved source
  Water system in buildings/ water system on facility grounds/public tap/borehole /protected well /protected rainwater collection
Water should be safely treated, reliable, sufficient and located at all points of care.

## Slide 11: Water needs and standards
Water should be available for
  drinking
  personal hygiene including hand washing, bathing and cleaning
  cleaning
  medical activities
  cooking
  laundry
Water must be on-site from an improved source
  Water system in buildings/ water system on facility grounds/public tap/borehole /protected well /protected rainwater collection
Water should be safely treated, reliable, sufficient and located at all points of care.
Droughts, floods, extreme weather events, sea level rise, and temperature increases can affect
availability
quality (including increased microbial contamination and salinity)
Functioning and safety of plumbing systems
Patient loads may increase during extreme weather events and COVID-19 response, putting a strain on a facility’s ability to respond.
Water utility workers, plumbers, and technicians may have restricted movements/be sick; supplies may be limited especially if imported or coming from capital cities

## Slide 12: Water requirements What should you be doing differently for COVID-19?
Water access: It is critical that health care facilities treating or who may treat COVID-19 patients have water.
Water quantity: Water, at a minimum for hand hygiene, cleaning and drinking.
Water quality: Drinking water should be from an improved source; ideally water should be treated and have chlorine residual.
Prepare: Contingency plans for limited water services and supplies.

## Slide 13: Types of “improved” water supply
Rainwater harvesting
Source: Compendium of water technologies. EAWAG, Switzerland. Forthcoming.
Solar powered borehole with piped-in network
Protected well with handpump

## Slide 14: Consider climate resilience of water supply technologies
Source: WHO, 2009. Vision 2030: The resilience of water supply and sanitation in the face of climate change. https://www.who.int/water_sanitation_health/vision_2030_9789241598422.pdf?ua=1

## Slide 15: WHO Standards for minimum water quantities in health care facilities
Out patients | 5 litres/consultation
In patients | 40–60 litres/patient/day
Operating theatre / maternity | 100 litres/ intervention
Dry or supplementary feeding centre | 0.5–5 litres/ consultation
Wet supplementary feeding centre | 15 litres/ consultation
Inpatient therapeutic feeding centre | 30 litres/ patient/day
Cholera treatment centre | 60 litres/ patient/ day
Severe acute respiratory diseases isolation centre | 100 litres/ patient/ day
Viral haemorrahagic fever isolation centre | 300–400 litres/ patient/ day
Source: WHO (2008). Essential environmental health standards in healthcare
. https://www.who.int/water_sanitation_health/publications/ehs_hc/en/
COVID-19 FAQ: How much water is needed for handwashing in resource-limited settings? The amount of water needed for handwashing is not well studied. If a tap was kept open for 20-40 seconds, about 2.5-5 litres per handwashing event would be needed (assuming a flow of 7.5 litres per minute). In resource-limited settings use of 0.5-2 litres per wash has been shown to reduce faecal contamination of hands.

## Slide 16: Quiz: Water quantity requirements
You are managing a primary care facility. It is open 7 days a week.
Each week, 10 women give birth at the facility.
Of these, on average, two women spend the night and the rest return home after a few hours.
In addition the staff treat, on average, 40 outpatients a week.
In addition, once a week a vaccination clinic is held which 50 children attend.
How much water does this facility need in one week?
© WaterAid
. https://www.who.int/water_sanitation_health/publications/ehs_hc/en/

## Slide 17: Answer
10 births x 100 litres /birth = 1,000 L
2 inpatients x 50 litres /patient = 100 L
40 patients x 5 L/patient = 200 L
50 children x 5 L/patient = 250 L
Weekly total = 1,550L
. https://www.who.int/water_sanitation_health/publications/ehs_hc/en/
© WaterAid
You are managing a primary care facility. It is open 7 days a week.
Each week, 10 women give birth at the facility.
Of these, on average, two women spend the night and the rest return home after a few hours.
In addition the staff treat, on average, 40 outpatients a week.
In addition, once a week a vaccination clinic is held which 50 children attend.

## Slide 18: Water uses and quality
A reliable drinking water station is present and accessible for staff, patients and carers, and those with disabilities at all times and locations/wards
Drinking water has appropriate chlorine residual (0.2mg/l or 0.5mg/l in emergencies) or free of E. Coli and not turbid.
Drinking water is safely stored in a clean bucket/ tank with cover and tap.
Sufficient energy is available for pumping and boiling water (mark if not applicable).
At least one shower or bathing area is available per 40 patients in inpatient settings and is functioning and accessible
Drinking water station in Thimpu, Bhutan

## Slide 19
What is wrong with these pictures?
What needs to be further assessed or investigated to confirm water safety?
More on water uses and quality
Notes: Add notes with answers to questions

## Slide 20: Focus on water STORAGE
Recalling the earlier example of a facility needing 1,550 liters of water a month
Which of the following storage containers do you recommend?
How does consideration climate resilience affect your decision?
© WaterAid

## Slide 21: Focus on water STORAGE
© WaterAid
5,000 liters
1,000 Liters
100 Liters
Facility uses 1,550 liters of water / week
1,550 liters / 7 days = 221 liters /day
Storage for 2 days = 221 x 2 = 442 liters
(+100 liters if births occur sequentially + 500 liters for climate resilience)
= 1,000 liters

## Slide 22: Spotlight on microbiological contamination of drinking-water
Microbial groups commonly associated with waterborne diarrhoea
Viruses
E.g. Hepatitis A, poliovirus A
Smallest; 0.02-0.3 μm
Protozoan cysts
E.g. Giardia, Cryptosporidium
Largest; >2 μm-2 mm
Bacteria
E.g. Escherichia coli, Vibrio cholerae
0.5-2.0 μm in diameter
Viruses
  E.g. Hepatitis A, poliovirus A
  Smallest; 0.02-0.3 μm
Bacteria
  E.g. Escherichia coli, Vibrio cholerae
  0.5-2.0 μm in diameter
Legionella:
Bacterium increasingly associated with waterborne outbreaks in health care facilities
https://www.who.int/water_sanitation_health/publications/legionella/en/
SARS-CoV2:
Enveloped virus; has not been detected in water supplies or water sources

## Slide 23: Drinking water & COVID-19
While the presence of the COVID-19 virus in untreated drinking-water is possible, it has not been detected in drinking-water supplies.
Other coronaviruses have not been detected in surface or groundwater sources  the risk of coronaviruses to water supplies is low.
COVID-19 is an enveloped virus. As such it has a fragile outer lipid membrane which makes it less stable, compared to non-enveloped viruses in the environment.
More susceptible to chlorine than other viruses
Ensure a residual concentration of free chlorine of ≥0.5 mg/L after at least 30 minutes of contact time at pH < 8.0.
Centralized distribution: chlorine residual should be maintained throughout the distribution system.

## Slide 24: What methods can you use to understand risks associated with water quality?
Sanitary inspection forms
Review of regulatory data
Check chlorine residual
Conduct fecal indicator bacteria testing
3
1
4
2

## Slide 25: Sanitary inspection forms
An on-site evaluation of all conditions, components and practices in the water supply system that pose an actual or potential risk to public health
Select appropriate form for facility’s water supply:
  Dug well with hand pump
  Deep borehole with motorized pump
  Public yard taps/piped distribution.
WASH FIT indicator: “Water supply poses low or no risk to public health, as measured by the Sanitary Inspection risk score”
Notes: Note, it is important that a SI form is completed as part of the field visit to a facility. If not, an optional classroom-based exercise is provided on the next slide.

## Slide 26: Exercise: conducting a “virtual Sanitary Inspection” form (Refer to handout: “Virtual SI exercise”)
30 mins
1. In groups, complete all sections of the SI form
2. Use the Technology Fact Sheet and Management Advice Sheet to help you complete the SI
3. Discuss the guiding questions (Page 3) as a group
Example: Dug well with a hand pump
Notes: If a field visit to a facility as part of the training is not possible, this exercise may be done instead. Refer to the handout for full instructions.
Adapting this exercise
The example provided is for a dug well with hand pump. For other settings, you may wish to adapt this example, e.g. using the rainwater collection and storage SI package.
Suggested energizer
Get the participants to stand in a line based on their total risk score (i.e. 0 to the left of the room, and 11 to the right). This gives a chance to explore the questions a bit more, and why some people scored differently than other etc. Why did the person on the right score so much higher than on the far left?

## Slide 27: Water treatment – making water safer
You are back at the facility.
The team conducted a sanitation inspection and found medium risk from the piped water supply. You check and there is no chlorine in the water. You spoke with the local regulator and the water in the past 30 days has exceeded E. Coli limits 10 times.
In the past 5 years there have been 3 major flooding events.
You decide to install water treatment. Furthermore, there is not reliable power at the facility.
What kind of treatment do you select and why?
© WaterAid

## Slide 28: Answers & discussion points
© WaterAid
Chlorination is important to provide ongoing disinfectant protection, especially as water supply is often faecally contaminated.
Floods will add a lot of organic matter, both naturally and from overflowing septic tanks  consider filtration.
Recommend an option that is off the grid due to unreliable power  consider a device that is solar powered or powered by a 12 volt battery.
Possible options include:
Ultra or nano Membrane filter + chlorination
Solar water pasteurization
Chlorine alone (need to increase dose or find alternative supply if water highly turbid during a flood)
Notes:   Technologies should meet one of WHO’s Household Water Treatment and Safe Storage (HWTS) performance categories and generally involve filters, boiling, Solar chlorine (for non-turbid water)
    coagulation/flocculation. Higher performing technologies (i.e. two or three stars including membrane filters, UV and coagulants/flocculants) are recommended for vulnerable groups (i.e. those with HIV or young infants) and where the specific pathogen of concern is not known. National water quality standards should exist and the facility water supply is regulated according to these standards.

## Slide 29: Where safely managed, treated piped water is not an option Choose wisely: 30 products tested, 6 fail
Comprehensive protection  or 
Aquasure TAB10
DayOne Waterbag™
Targeted protection 
Tulip Table Top Water Filter
Uzima Filters UZ-01
Little or no protection
−
Biocool CleanWater
LifeFilta LFJC Jerrycan
GrifAid®M3
Chloritard
SPOUTS Water Purifaaya Filter
Nazava Water Filter
Water Elephant
Aquatabs Flo
BlueQ™ 2-stage
Mesita Azul °
Aquapak
JAMEBI Solar Water Pasteurizer
SolarBag®
WATA-Standard™
Oasis Water Purification Tablets*
Silverdyne
Tembo ceramic pot
Lifestraw Family 1.0
Lifestraw Famly 2.0
Lifestraw community filter
P&G Purifer of H20
Wadi Solar
H2g0 Purifier
Aquatabs
WHO Scheme to Evaluate Household Water Treatment Performance
https://www.who.int/water_sanitation_health/water-quality/household/scheme-household-water-treatment/en/

## Slide 30: Climate resilient water supplies
Raised water storage tanks
Back-up water supplies in event of drought, flooding, power outages
Use of renewable power (e.g. solar)
Re-use of greywater/washwater for watering grounds, flushing toilets

## Slide 31: Safe plumbing
Plumbing should not have any cross connections (e.g. between safe water supply and contamination)
Piping connections should be regularly checked and leaks fixed
Safe water pipes should be placed above black or grey water pipes to avoid cross contamination
Bathroom showers and sprayers should have backflow protectors to prevent blackwater or fecal matter entering system
After an adverse event where water quality is compromised, treatment should be used and water system flushed.
What risks, linked to unsafe plumbing, do you notice in this photo?

## Slide 32: Water management Spotlight on Legionella
Legionella: a bacteria that naturally occurs in freshwater and can multiply under certain conditions
Legionella can cause Legionellosis: people contract this disease by inhaling small droplets of the contaminated water through mist or vapor.
Legionella grows best in lukewarm water (25°C - 43°C).
Image: Guidelines for Legionella control. Australian Government. 2015
Notes: Legionella are naturally occurring bacteria found in freshwater sources, such as rivers and lakes, where the bacteria generally are present in low amounts and do not lead to disease.³
However, Legionella can multiply to dangerous levels under certain conditions and potentially cause Legionnaires’ disease, or Legionellosis. People contract this disease by inhaling small droplets of the contaminated water through mist or vapor.
Excessive water age. The longer water sits in a system or piping in a system, the greater likelihood the water disinfectant will dissipate over time, leading to pathogen growth.⁸
Biofilm. When biofilm, a sticky substance created by bacteria, forms on the inside wall of water supply piping, it protects Legionella from heat and disinfectant.⁹
Lukewarm water. Legionella growth is enabled by lukewarm water temperatures, usually in the range of 77 degrees Fahrenheit to 108 degrees Fahrenheit.⁹
Insufficient disinfectant. Effective water disinfectant strategies are necessary to control Legionella in a water system. For example, chlorination is one method used by water districts to disinfect drinking water that provides a lasting residual disinfectant.¹⁰
Inadequate corrosion control. Corrosion can occur in system pipes, depending on several water quality variables, including disinfectants used, water temperature and pH levels. Improper corrosion control can create the ideal environment for Legionella growth.¹¹
Cross connections. Cross connections between potable and non-potable water can introduce Legionella into the potable water supply system.¹²

## Slide 33: What would you do to prevent Legionella?
Keep hot and cold water outside growth range of Legionella (i.e. hot water at point of distribution > 50°C)
Ensure there are no cross connections between potable and non-potable water
Regularly monitor and adjust disinfectant dose to achieve minimum concentration at point of distribution (>0.2 mg/l chlorine)
Ensure there is no stagnant or low flow water in the water system.
Develop and implement a water risk management plan considering the factors above.
https://www.who.int/water_sanitation_health/publications/legionella/en/

## Slide 34: WASH FIT essential WATER indicators
SUPPLY: Improved water supply is piped into the facility or on premises
Additional improved source(s) identified and can be accessed in case main source is no longer functioning/available.
AVAILABILITY: Water services available at all times throughout the day (and night, if facility is open)
Water services available throughout the year (i.e. not affected by seasonality, climate change-related extreme events or other constraints)
QUANTITY: Water of sufficient quantity for all uses
SAFE STORAGE: Safe water storage exists to meet needs of facility for two days
DRINKING WATER: Safe drinking water is available and accessible for staff, patients and carers at all times in main waiting areas and/or entrance to each ward and in all rooms where patients stay overnight or receive specialized care.
Drinking-water has appropriate chlorine residual (0.2mg/L or 0.5mg/L in emergencies) or 0 E. coli/100 ml.
SURVEILLANCE: The facility water supply is routinely tested by a staff member/and or independent authority (e.g. the surveillance agency)
Most recent water quality testing results confirm that water quality meets national water quality standards

## Slide 35: Key takeaways
Water is fundamental for providing safe and clean care and for respecting the dignity and rights of staff, patients and caregivers
Water quantity needs depend on the types of services and number of patients and their caregivers
The risk of coronaviruses to water supplies is low
When possible, water should be treated: many low-cost options exist
Climate resilient water systems require back-up supplies, storage, additional treatment and infrastructure that can withstand floods, droughts and extreme events
Legionella can be prevented through good water system management.

## Slide 36: Questions?

## Slide 37: References
WHO. (2008). Essential environmental health standards in health care.
WHO. (2011). Technical notes on drinking water, sanitation and hygiene in emergencies. http://www.who.int/water_sanitation_health/publications/2011/tn9_how_much_water_en.pdf
WHO, 2007. Legionella and the prevention of Legionellosis. www.who.int/water_sanitation_health/emerging/legionella_rel/en/index.html
WHO, 2017. Guidelines for drinking-water quality, 4th edition. www.who.int/water_sanitation_health/publications/drinking-water-quality-guidelines-4-including-1st-addendum/en/
WHO Water safety and quality https://www.who.int/water_sanitation_health/water-quality/en/
WHO International Scheme to Evaluate Household Water Treatment Technologies https://www.who.int/water_sanitation_health/water-quality/household/scheme-household-water-treatment/en/
HOUSE, S.; REED, B. (1997): Emergency Water Sources. Guidelines for Selection and Treatment. Loughborough: Water, Engineering and Development Centre (WEDC). URL: http://sheltercentre.org/sites/default/files/Emergency%20Water%20Sources%20%28WEDC%29.pdf