## Slide 1
Better WASH for quality care in HEALTHCARE FACILITIES
Technical Module:
HEALTH CARE WASTE MANAGEMENT
Insert date & location

## Slide 2: Learning objectives
By the end of the session, participants should:
Understand the process of health care waste management from generation to safe treatment and disposal
Know which waste treatment options are the most environmentally-friendly and be aware of mitigation measures against climate change
Know how to ensure waste infrastructure is resilient to the effects of climate change, including extreme weather events
Know how to reduce the risks caused by unsafe health care waste management practices in health care facilities

## Slide 3: What is wrong in this picture?
Notes: Waste is:
Not segregated: yellow and black bags are all mixed together
Exposed: intravenous lines open dumped
No fence – open area. Dogs and other animals may scavenge, not protected from human contact.

## Slide 4
Notes: Top left: broken black bag with sharp waste (needle is pricking through – usage of a black bag instead of a yellow)
Top right pic: dog puppies in a placenta pit (unprotected pit – dogs can spread infectious)
Bottom left: dog puppy sleeps in an open dump with hazardous and non-hazardous waste mixed
Bottom middle: overfilled and broken bin for infectious waste – unprotected and accessible to the public.
Bottom right: overfilled small-scale incinerator (risk for the operator – incinerator should be heated up before starting to be filled)

## Slide 5: Health care waste indicators for WASH FIT
SEGREGATION: Availability of bins, waste segregated correctly, guidance of waste segregation clearly visible
REDUCTION & RECYCLING: Strategies to tackle waste “at source”
STORAGE: waste stored within safe time limit, storage areas are safe, waste stored separately according to type
TREATMENT: availability and safe management of technologies; availability of fuel/energy for operation
DISPOSAL: functional pit/waste dump or municipal pickup, pits can withstand climate emergencies, availability of pathological waste pit
PHARMACEUTICAL WASTE: safe treatment & disposal
PPE: availability of PPE and hand hygiene for waste handlers
OCCUPATIONAL HEATLH: waste handlers are vaccinated
Notes: This is presented up front to show what will be covered in the module.

## Slide 6: Waste management process
Start: Waste minimization
Transport
Storage
Treatment
Final disposal
Segregation
Collection
Segregation is the key to waste management:
all other steps depend on effective segregation
Notes: The logistic chain starts with MINIMISATION – not to produce waste or to produce less waste, lowers the risk for humans and environment in general – and also lowers costs!
Segregation is the key to the waste management system: all other logistic steps (collection, transport, storage, treatment and disposal) are based on this step!

## Slide 7
What is the typical composition of waste generated in a health care facility?
Between XX% and XX% of the waste produced is similar to domestic waste and usually called ‘non-hazardous’ or ‘general health care waste’
XX - XX% of health care waste is regarded as ‘hazardous’ and may pose a variety of environmental and health risks
Safe management of waste from health-care activities, WHO, 2014
https://www.who.int/water_sanitation_health/publications/safe-management-of-wastes-from-healthcare-activities/en/
Notes: Quiz – ask participants to guess their answers.
Virtual audience adaptation: This could be done by Zoom poll, Mentimeter or similar programme.

## Slide 8: What is the typical composition of waste generated in a health care facility?
Between 75% and 90% of the waste produced is similar to domestic waste and usually called ‘non-hazardous’ or ‘general health care waste’
10-25% of health care waste is regarded as ‘hazardous’ and may pose a variety of environmental and health risks
Safe management of waste from health-care activities, WHO, 2014
https://www.who.int/water_sanitation_health/publications/safe-management-of-wastes-from-healthcare-activities/en/
Non-hazardous waste is usually similar in characteristics to municipal solid waste. More than half of non-hazardous waste from hospitals is paper, cardboard and plastics, whilst the rest comprises discarded food, metal, glass, textiles, plastics and wood.
Notes: The 10% of infectious waste also includes sharp waste and pathologic / anatomical waste (biohazardous waste)

## Slide 9: How much infectious waste is generated in a typical facility per day?
Capacity of waste treatment technology needed
Hospital: Waste generation rate per day x the number of beds x bed occupancy rate
Clinic/basic health unit: Waste generation rate per day x the average number of patients / day

## Slide 10: What are some common examples for each category of waste?
Category | Examples
Sharps waste | Used or unused sharps (i.e. hypodermic, intravenous or other needles; auto-disable syringes; syringes with attached needles; infusion sets; scalpels; pipettes; knives; blades; broken glass
Infectious waste | Waste suspected to contain pathogens and pose a risk of disease transmission (i.e. waste contaminated with blood and other body fluids; laboratory cultures and microbiological stocks
Pathological waste | Human tissues, organs or fluids; placenta, body parts; unused blood products
Pharmaceutical waste, cytotoxic waste | Pharmaceuticals that are expired or no longer needed; items contaminated by or containing pharmaceuticals Cytotoxic waste containing substances with genotoxic properties, e.g. waste containing cytostatic drugs (used in cancer therapy); genotoxic chemicals
Chemical waste | Waste containing chemical substances (i.e. laboratory reagents; film developer; disinfectants that are expired or no longer needed; solvents; waste with high content of heavy metals, e.g. batteries; broken thermometers and blood pressure gauges)
Radioactive waste | Waste containing radioactive substances (i.e. unused liquids from radiotherapy or laboratory research; contaminated glassware, packages, or absorbent paper; urine and excreta from patients treated or tested with unsealed radionuclides; sealed sources)
Notes: Pathological waste might also include anatomical waste (amputated body parts).
Chemical waste also includes portable pressurized cylinders, cartridges and aerosol cans – depending on the content these can also be considered as general waste.
Note: Waste from X-ray departments are NOT radioactive. It is categorized as chemical waste (fixer, developer, x-ray films).

## Slide 11: What are some common examples for each category of waste?
Category | Examples
Sharps waste | Used or unused sharps (i.e. hypodermic, intravenous or other needles; auto-disable syringes; syringes with attached needles; infusion sets; scalpels; pipettes; knives; blades; broken glass
Infectious waste | Waste suspected to contain pathogens and pose a risk of disease transmission (i.e. waste contaminated with blood and other body fluids; laboratory cultures and microbiological stocks
Pathological waste | Human tissues, organs or fluids; placentas; body parts; unused blood products
Pharmaceutical waste, cytotoxic waste | Pharmaceuticals that are expired or no longer needed; items contaminated by or containing pharmaceuticals Cytotoxic waste containing substances with genotoxic properties, e.g. waste containing cytostatic drugs (often used in cancer therapy); genotoxic chemicals
Chemical waste | Waste containing chemical substances (i.e. laboratory reagents; film developer; disinfectants that are expired or no longer needed; solvents; waste with high content of heavy metals, e.g. batteries; broken thermometers and blood pressure gauges)
Radioactive waste | Waste containing radioactive substances (i.e. unused liquids from radiotherapy or laboratory research; contaminated glassware, packages, or absorbent paper; urine and excreta from patients treated or tested with unsealed radionuclides; sealed sources)

## Slide 12: Segregation
Different types of waste require different handling, treatment and disposal
Segregation must start at the source, i.e. where waste is generated
In most wards three waste categories are generated and should be segregated accordingly:
  General waste
  Infectious waste
  Sharp waste
Health care Waste
3-bin Standard System
General waste
Infectious
Sharp waste
Notes:   Basic (all patient care areas) = 3 bins
    Bin for general waste (black bag in a bin)
    Bin for infectious waste (yellow bag in a labeled pedal bin)
    Sharp container or needle cutter

## Slide 13: Three-bin system for basic waste categories: Example poster
Black container (lined)
Yellow container (lined)
Sharps box
Notes: In some countries infectious waste is color coded with red. It is just a different system – not wrong – but it be used as standardized in the country.

## Slide 14: Non-hazardous/ general waste
Waste that does not pose any particular biological, chemical, radioactive or physical hazard
Can be disposed of as household waste through available landfills / municipal waste disposal sites / facility waste pit
Some can be recycled (e.g. paper) or composted
Notes: More than 50 % of non-hazardous waste from hospitals is recyclable, e.g. paper, cardboard and plastics!

## Slide 15: What are common examples of household waste found in a health care facility ?
Packaging materials (papers, cartons, sacks)
Plastic bottles & cans
Food remains
Dry grass and leaves
Broken/old equipment or furniture (e.g. sofa, chairs)

## Slide 16: Methods for disposing of sharps
Notes: Top
1. Two bins with correct label and colored bag – poster support segregation
The use of pedal bins is recommended in order not to touch the lid of the bin
In case there is a lack of sharp container, self-made ones are an option (labels are produced locally)
The use of a needle cutter (needle is cut from the syringe body):
Bottom:
5-liter cardboard sharp container (UN / WHO standard)
Needle strip sharp box: the needle is striped off the syringe body (sharp box can be used for a longer time)
Ward setting : labeled and lined black and yellow bin plus a sharp containers at the trolley

## Slide 17: Guidance for bins and containers
Waste categories | Colour and markings | Type of container | Collection frequency
Infectious waste |  | Leak-proof strong plastic bag placed in a container (bags for highly infectious waste should be capable of being autoclaved). | When three-quarters filled or at least once a day.
Sharp waste |  | Puncture-proof container. | When filled to the line or three-quarters filled.
Pathological waste |  | Leak-proof strong plastic bag placed in a container. | When three-quarters filled or at least once a day.
Chemical and pharmaceutical waste |  | Plastic bag or rigid container. | On demand.
Radioactive waste |  | Lead box. | On demand.
General health-care waste | Black or grey coloured bag | Plastic bag inside a container or container which is disinfected after use. | When three-quarters filled or at least once a day.

## Slide 18: How to select the best technology?
B) Interim waste treatment technologies used in low resource settings
A) Compliance with the Stockholm and Basel Conventions
National & international regulations
Available budget (for investment and maintenance)
Infrastructure (space)
Available energy (electricity, water, fuel etc.),
Type & quantity of waste generated
Available final disposal options (recycling, landfill)
https://www.who.int/water_sanitation_health/publications/technologies-for-the-treatment-of-infectious-and-sharp-waste/en/
Notes: Optional slide for background information, not to be included in the training.

## Slide 19: Heirarchy of waste treatment options
https://www.who.int/water_sanitation_health/publications/technologies-for-the-treatment-of-infectious-and-sharp-waste/en/
Notes: The green highlighted waste treatment options should be preferred as these are limiting the emissions to the environment (autoclave does not emit emissions, emissions from incineration can be cleaned by a flue gas cleaning system).
The yellow highlighted which can be used as interim solutions.
The red ones are considered as the last resort options and are not recommended but sometimes the only feasible option for emergency or as an interim solution. These process should be minimized and eliminated as soon as possible and wherever feasible.

## Slide 20: Alternative treatment of infectious and sharp waste
Treatment by steam ~121°C or ~134°C
No hazardous emissions or ash
Can only be used for infectious / sharp waste
After treatment the waste is considered as non-hazardous, some can be recycled
However, needs reliable water and electricity connection!
Alternative treatment options for infectious waste (low heat)

## Slide 21: Incineration: Stockholm Convention
Commonly used in low-resource settings
Low cost, easy to install, but generate hazardous emissions ….
Must comply with the Stockholm Convention:
  2 burning chambers (1st: 850 °C and 2nd: 1,100°C),
auxiliary burners and fuel supply
sufficient resident time of air in the 2nd chamber
sufficient oxygen content and
high turbulence of exhaust gases
As well as flue gas treatment
Stockholm Convention is a legally binding treaty to protect human health and the environment from POPs. Parties are required to use the BAT and BEP limit the levels of dioxins and furans in air emissions to 0.1 ng I-TEQ/Nm3.
Notes: Disadvantage: release of combustion by-products into atmosphere and generation of residual ash, which is hazardous for health and environment.
Combustion by-products are dioxin and furans (POPs).
Dioxin and furans causes negative effects on the environment and health of humans including:
skin toxicity,
immunotoxicity, neurotoxicity,
negative effects on reproduction,
teratogenicity,
Endocrine disruption, and a predisposition to cancer
POPs: Persistent Organic Pollutants (POPs) are toxic substances composed of organic (carbon-based) chemical compounds and mixtures. They include industrial chemicals like PCBs and pesticides like DDT. They are primarily products and by-products from industrial processes, chemical manufacturing and resulting wastes.

## Slide 22: If using incineration, which items must not be incinerated?
Pressurized gas containers
Sealed ampoules or vials (explode in the chamber)
Chemical waste (e.g. reactive chemicals, aldehydes)
Halogenated materials (e.g. PVC plastics)
Waste containing mercury, cadmium and other heavy metals
Radioactive waste
These items pollute the environment, produce hazardous reactions or are explosive
Notes: Reactive chemicals from the lab
photographic waste from x-ray,
Aldehydes from the pathology lab
Heavy metals like mercury containing thermometer, fluorescence bulbs…
Halogenated elements: fluorine, chlorine, bromine, or iodine

## Slide 23: Healthcare waste staff
A responsible person for the management of healthcare waste should be appointed and trained (Healthcare Waste Officer – HWO)
This person is often from the Infection Control Committee
The HWO should be trained on HCWM
Introduction of supervision
of safe handling methods
Data recording
Supervision of safe waste treatment and disposal
Development and revision
of a waste management plan
Observing
legal regulations
Regular training of
medical and logistic staff
Notes: In a lot of countries the HWO is the Infection Control Nurse or the Head Nurse.
The duties of the HWO should be included in the description of the person taking this position.

## Slide 24: Safe appropriate collection
A schedule should be available for reference: e.g. collection of waste after each shift.
PPE use and hand hygiene action should be followed
Waste bags should be collected when 3/4 full or at least daily
Sharp waste should be collected when the container is 3/4 full
Hazardous and non-hazardous waste should never be collected at the same time as then all waste has to be considered hazardous
Tie bags securely
After removing the waste bag, replace with a new one

## Slide 25: Safe and appropriate transport
Waste handlers should wear appropriate PPE and perform hand hygiene after handling waste or if hands get contaminated at any time
Transport waste with covered trolley, wheel barrow, wheeled bin or cart
Separate transport of hazardous and non-hazardous waste (yellow - black)
Transport equipment should be dedicated for waste transportation only
The equipment must be cleaned and disinfected at the end of each working day, PPE should be worn, and hand hygiene performed afterwards
Notes: Disinfection of bins: e.g. chlorine (0.2%) solution
Washing / disinfection areas should be available also for the waste handlers – like the persons transporting the waste!

## Slide 26: Waste storage area: non-hazardous waste
Size of storage areas according to the quantities / volume of waste generated and the frequency of collection
Fenced and paved
Easy access for municipal waste collection trucks
Where recycling takes place, separate areas for recyclables should be available
Notes: A roof is recommended to prevent that the container are filling up with water and to keep the waste away from direct sun (depending on the rainfall in the country)

## Slide 27: Waste storage: infectious & sharp waste
Only infectious and sharp waste should be stored here – no mixture with other waste.
Inaccessible to unauthorized persons, animals, insects and birds
Marked with biohazard symbol
Floor and walls are sealed or tiled to allow easy disinfection
Keep well ventilated & protected from rain
Notes: The flow of waste building for the storage and treatment of infectious and sharp waste should be from hazardous towards non-hazardous:
-
Entry of the waste through the reception room, where it is weighted and documented.
- Then it is stored.
- From there it is taken to the treatment equipment. The empty bins can be cleaned and in case of the use of an autoclave or other alternative treatment technology the waste is disposed as general waste.

## Slide 28: Storage times for infectious waste and pathological waste
Waste can be stored for the time between waste generation and treatment
Storage should not exceed the following periods:
Temperate climate: 72 hours in winter 48 hours in summer | Warm climate: 48 hours during the cool season 24 hours during the hot season
Source: Safe management of waste from health-care activities, WHO, 2014
Note: waste can be stored for more than a week when stored below 8° C (e.g. in a fridge or in winter with temperatures below 8 °C)
Note: sharp waste can be stored longer! It should be collected and stored for treatment when ¾ filled.
Notes: Note: sharp waste can be stored longer! It should be collected and stored for treatment when ¾ filled.

## Slide 29: Disposal of general waste: Sanitary Landfill / Protected Pit
Municipality: Lined landfill to prevent leachate from contaminating the environment (preferable)
Low resource setting: protected pit at the healthcare facility (interim solution)
Source: Safe management of waste from health-care activities, WHO, 2014
Notes: Landfill: waste is isolated from the surrounding environment (groundwater, air, rain). This isolation is accomplished with a bottom liner and daily covering of soil. A sanitary landfill uses a clay liner to isolate the trash from the environment.

## Slide 30: Disposal: Ash and Placenta Pits
Source: Technical Specifications, Health Care Without Harm / MSF
Notes: Not accessible to unauthorized persons (fenced, locked)
If possible, located on a higher-level area - bottom should be 1.5 meter away from the water table.
Ash pit should be lined with watertight bricks or concrete lining to prevent contamination to the soil and water (ash is considered as hazardous waste)
Placenta pit does not need to be entirely lined, with concrete, as it is biodegradable and will sooner or later be transferred to soil.

## Slide 31: Biodigestion
Can treat food and pathological waste
Two chambers increase retention time, pathogens die naturally
Digested waste flows into sewers without further handling
Biogas can be used as fuel for cooking or water heating
Notes: - Biodigesters can be a valuable waste disposal option for any facility which has large amounts of organic waste, especially pathological waste like placenta, and food or kitchen scraps.
- They consist of large underground chambers, built of brick or concrete, and are often seeded with cow dung which provides bacteria to break down the waste.
- Having two digestion chambers, one after the other, keeps the placenta in the systems for long enough- at least 90 days is recommended- for any pathogens to degrade.
- Some water is added along with the waste, to keep the contents of the chamber liquid enough to flow freely. As more waste is put into the digester, digested waste overflows at the other end, into the sewer or septic tank. This means that the waste never needs to be handled again, which adds another layer of safety.
- As the waste breaks down, it creates biogas, which has a high content of methane and can be used as a renewable fuel. The easiest and most efficient uses are cooking and water heating.
- An experienced designer and construction company are needed, though there is often national level experience in the WASH and agricultural sector. A well built digester needs little maintenance and can last for over 20 years.
How common are biodigesters and how easy/difficult are they to install?
They are not yet well established, but excellent examples in Nepal as well as our own in Tanzania and I know of one in Zambia. They require expert design and installation- but that is true of all technologies. Also, many countries have good expertise in the WASH or agricultural sector, so cross-fertilisation is possible.
Are they predominately in hospitals or in smaller facilities too? What incremental improvements could be used?
The incremental change could come from piloting at some of the larger HCFs, and then moving down the chain as it becomes more established. Technically, it can be done at a small HCF, but neither the need nor the benefit are so large. Below 10-12kg of waste per day, the gas produced will be very limited and may not be of great interest to the HCF staff.
This blog may be useful. https://greengrowthknowledge.org/blog/win-win-disposing-medical-waste-biodigestion

## Slide 32: Documentation
The following documentation should be available:
  Standard Operation Procedures (SOPs) / Protocols (e.g. for segregation, collection, transport, storage, treatment, disposal, spillages):
    Possible Hazards,
    Responsible Person, Emergency Contact,
    Step for step procedure, dos and don’ts.
  Incident Reports (sharp incidents etc.)
  Weighing records of the generated infectious and sharp waste
Notes: Do you have a reporting system on needle stick incidents in your facility or/ and on national level?
How is the standardized procedure for a needle stick incident (who need to be informed, medical care, filling out forms)?
Why is it recommended to weigh the infectious waste?
- To observe changes in the amount generated and to invest on mitigation measures.
To proof that the implemented activities to improve segregation and minimization are working.
To plan for sizes and capacities of storage, treatment and disposal of this waste.

## Slide 33: Safe handling of waste for health care workers
When handling hazardous or infectious waste, always wear personal protective equipment (PPE). It provides barriers and filters between workers and the hazard. PPE should include:
Heavy duty gloves
Mask/goggles or face shield
A long sleeved gown/apron
Closed shoes are also important
Depending on the task a hard hat may be recommended
Remove PPE and perform hand hygiene after the task/
handling waste
Health care waste worker wearing PPE, Kenya
Notes: Wear appropriate personal protective equipment (PPE)
Handle waste with care
Practice hand hygiene before and after handling waste
Do not re-sort waste
Never carry waste bags/containers against body
Avoid heavy loads (use transport tools)

## Slide 34: How to increase sustainability of waste practices?
Stakeholders must be convinced that proper HCWM is important for health and environment!
Legal framework, rules and guidance is available, standardized, known and available for all
Training on HCWM need to be part of the country / district / facility organization / culture (institutionalization)
Adequate budget for HCWM is available
Equipment and infrastructure is
maintenance and repaired
Continuous monitoring and mentoring…
Notes: What could you do to increase sustainability in your facility?

## Slide 35: Climate change impacts on healthcare waste management
Solid waste management can exacerbate negative effects on climate, due to the emission of greenhouse gasses like CO, CH and NO by incineration and landfilling (methane - 28x the Global Warming Potential of CO)
Changes in hydrology and temperature can affect the stability of waste containment structures
Increased rainfall and flooding can affect waste containers and lead to spreading of contaminants (including hazardous).
If there is flooding in areas near the facility (even if facility itself is not flooded), there can be disruption of the waste management chain (e.g. flooding of road, railway affect waste collection and off-site treatment).
Low lying coastal facilities are at increasing risk from flooding.
Notes: Solid waste management can have exacerbating effects on the climate especially due to the emission of greenhouse gasses: Transporting health care waste in vehicles using fossil fuels, inadequate incineration, inappropriate incinerator technology, or the incineration of unsuitable materials results in GHG emissions and the release of pollutants into the air
Changes in hydrology and temperature can affect the stability of waste containment structures (e.g. waste pits) within the health care facility
Increased rainfall and flooding can lead to inundation of the facility and affect waste containers with spreading of contaminants (including hazardous). Consider this risk when planning and checking waste containers - placement and protection.
Even if facility is not flooded but the surroundings are, there can be disruption of the waste management chain (e.g. flooding of road, railway affect waste collection and off-site treatment), so extra containment capacity needs to be in place at the facility.
Low lying coastal facilities are at increasing risk from inundation.
CO = carbon dioxide, CH = methane and NO = nitrous oxide
Solid waste management can have exacerbating effects on the climate especially due to the emission of greenhouse gasses: Transporting health care waste in vehicles using fossil fuels, inadequate incineration, inappropriate incinerator technology, or the incineration of unsuitable materials results in GHG emissions and the release of pollutants into the air
Changes in hydrology and temperature can affect the stability of waste containment structures (e.g. waste pits) within the health care facility
Increased rainfall and flooding can lead to inundation of the facility and affect waste containers with spreading of contaminants (including hazardous). Consider this risk when planning and checking waste containers - placement and protection.
Even if facility is not flooded but the surroundings are, there can be disruption of the waste management chain (e.g. flooding of road, railway affect waste collection and off-site treatment), so extra containment capacity needs to be in place at the facility.
Low lying coastal facilities are at increasing risk from inundation.
CO2 = carbon dioxide, CH4 = methane and N2O = nitrous oxide

## Slide 36: Adapting healthcare waste management in response to climate change
Waste prevention and reduction: strategies are employed which result in a reduction in the quantity of waste generated
Waste recycling: Non-hazardous waste is safely recycled
Sufficient waste containers are in stock and/or frequency of emptying planned and resourced in case demands on health care facilities increase
Safe storage capacity is available for additional waste generated during climate-events and/or emergencies
Recovery Efforts after Dumpsite Collapse from Heavy Rains in Colombo, Sri Lanka

## Slide 37: Healthcare waste management contribution to mitigate climate change
Phase out of incineration of medical waste: non-burn technologies are available to safely disinfect, neutralize or contain waste (e.g. autoclaves)
While incineration is phased out: Cardboard sharps/safety boxes are used in place of plastic boxes, to reduce harmful emissions when burned
Pit/waste dump: In case of flooding, an alternative is in place including storing waste in elevated containers and/or transporting off-site
Waste pits are watertight to avoid flooding and are not over filled
Autoclave treatment of medical waste
Notes: Note: Autoclaves are closed chambers that apply heat and sometimes pressure and steam, over a period of time to sterilize medical equipment. Autoclaves have been used for a century to sterilize medical instruments for re-use.

## Slide 38: Key takeaways
Segregate hazardous and non-hazardous waste at the point of generation
Use sharp boxes – never recap or reuse needles
Keep infectious and sharp waste away from patients and public
Treat infectious and sharp waste before disposal
Plan for incremental improvement of your waste management system
As much as possible, adapt waste systems to reduce negative impact on climate

## Slide 39: Health care waste in the context of COVID-19
Note: There is no evidence that direct, unprotected human contact during the handling of health care waste has resulted in the transmission of the COVID-19 virus.
Enforce or re-enforce best practices for HCWM, including assigning responsibility and sufficient human and material resources to treat and dispose of waste safely.
General waste: segregated from infectious in clearly marked bins, bagged and tied, and disposed as general municipal waste.
Infectious waste: produced during patient care, including those with confirmed COVID-19 infection (e.g. sharps, bandages, pathological waste) - collected safely in clearly marked lined containers and sharp boxes.
  Infectious waste should be treated, preferably on-site with alternative treatment technologies like autoclaving, and then safely disposed.
If waste is moved off-site, it is critical to understand where and how it will be treated and disposed.
Notes: Source:
Water, sanitation, hygiene, and waste management for SARS-CoV-2, the virus that causes COVID-19
Interim guidance
29 July 2020

## Slide 40: Prepare for extra waste generation: Increase waste management capacity!
Waste generated in waiting areas of health care facilities or at home during home based quarantine can be classified as non-hazardous and should be packed in strong black bags and closed properly before disposal by municipal waste services.
  If waste services not available: interim solutions like safe burying or controlled burning might be considered.
It is important to asses the existing waste treatment capacity as the volume of waste during an outbreak will increase (mainly PPE) and additional treatment capacity might be needed.
For more information refer to the WHO guidance, Safe management of wastes from health-care activities (32).
Waste handlers:
wear appropriate PPE (boots, long-sleeved gown, heavy-duty gloves, mask, and goggles or a face shield) and
perform hand hygiene after removing it.
Note: .
A surgical or even a cloth mask can protect
against splashes and also help prevent workers touching their faces (N95, FFP2 or 3 masks are not essential).

## Slide 41: Encapsulation & burning pits A solution for emergency settings
Encapsulation (disposal of expired vaccines & medications)
  Add immobilizing materials (i.e. cement) and seal the container
Burning pit
  Disposal of waste only during emergency in the absence of incinerators/autoclaves.
  It causes higher smoke pollution and other health risks
Notes: Expired pharmacies can also be inerted. Inertization is a variant of encapsulation and involves removing the packaging materials, paper, cardboard and plastic, from the pharmaceuticals. Pills need to be removed from their blister packs. The pharmaceuticals are then ground, and a mix of water, cement and lime added to form a homogenous paste. More information:
https://www.who.int/water_sanitation_health/publications/unwanted-pharmaceuticals/en/
Burning in a pit should be undertaken in a confined area – away from public and the health facility. The waste should be burned within a dugout pit, followed by covering with a layer of soil

## Slide 42: Questions?

## Slide 43: References
UNEP (2003). Technical guidelines on the environmentally sound management of biomedical and healthcare waste. http://archive.basel.int/pub/techguid/tech-biomedical.pdf
UNEP (2007). Guidelines on best available techniques and provisional guidance on best environmental practices relevant to Article 5 and Annex C of the Stockholm Convention on Persistent Organic Pollutant. http://chm.pops.int/Implementation/BATandBEP/BATBEPGuidelinesArticle5/tabid/187/Default.aspx
WHO (1999). Guidelines for safe disposal of unwanted pharmaceuticals in and after emergencies. http://apps.who.int/medicinedocs/en/d/Jwhozip51e/
WHO (2003a). Aide-memoire for a strategy to protect health workers from infection with bloodborne viruses. http://www.who.int/occupational_health/activities/1am_hcw.pdf
WHO (2014). Safe management of wastes from health-care activities. http://www.who.int/water_sanitation_health/publications/wastemanag/en/
WHO (2017). Safe management of wastes from health‑care activities - A summary;” https://www.who.int/water_sanitation_health/publications/safe-management-of-waste-summary/en/
WHO (2019). Overview of technologies for the treatment of infectious and sharp waste from health care facilities”; https://www.who.int/water_sanitation_health/publications/technologies-for-the-treatment-of-infectious-and-sharp-waste/en/index.html